## SUMMARY
April 21th, 2018
BOQ GRAND SUMMARY
1 | DESCRIPTION | AMOUNT | REMARKS
A | CIVIL
B | CARPENTRY
C | CEILING, PARTITIONS,WALLS & FINISHES
D | CCTV & NETWORKING WIRING
E | FIRE FIGHTING
F | ELECTRICALS
G | FURNITURE
H | AIR CONDITIONING
SUMMARY
NOTE : ALL APPLICABLE TAXES TO BE CHARGED EXTRA GST 18%.
PRICES MAY VARIES AFTER FINAL SLD & AS PER SIDE CONDITION.

## CIVIL
CIVIL (A)
S.No | DESCRIPTION | UNIT | QTY | RATE (Rs.) | AMOUNT | REMARK
(A ) | CEMENT PLASTER
A
1 | Providing and rendering 15 mm thick cement plastering on surfaces in two layers consisting of 4 mm thick sand faced plaster in cement mortar 1:4 (1 cement :4 fine sand) top coat mixed with integral water proofing compound and specified fibers over a base coat of 10 mm thick rendering in cement mortar 1:4 (1 cement :4 coarse sand), forming key to receive the finishing coat including necessary scaffolding and curing etc.complete at all heights. | SQFT | Rate Only
2 | BRICK WORK : 4.5'' BRICKWORK IN HALFBRICK MASONARY RED BRICKS CLASS DES. 7.5 in 1:4 cement mortar | SQFT | Rate Only
TOTAL PLASTER SUMMARY

## CARPENTRY
CARPENTRY (I)
S.No | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
1 | WOODEN GLASS PARTATION : P & F of laminated wooden glass Partation with 8mm thk. Tuffan glass. | SQFT | 869 |  | 0
2 | WOODEN DOORS : P & F 35 mm thk. Wooden Laminated Door with Complete Hardware of cylender Lock, Handle, Concled Door Closer, Stopper etc. Ozone/ Doorset, with 80x50mm thk wooden door frame DOOR SIZE upto ( 1000 X 2100) | NO | 4 |  | 0
3 | WOODEN PANELLING : P & F Wooden Wall Pannaling made of 2"x2" wooden frame with 9mm thk ply. Finish with approved shade of laminate. | SQFT | 100 |  | 0
4 | RECEPTION BACK WALL (10'8" X 9'6") | SQFT | 100 |  | 0
5 | DISPLAY & STORAGE : P & F of Full ht. Laminated Display Storage Unit 400 to 500 deep with 6mm thk. tuffan glass shutters | SQFT | 250 |  | 0
6 | CUBBOARD STORAGE : P & F of Full/Mediam/Low ht./overhead Laminted Storage finish with approved shade of laminate. | SQFT | 300 |  | 0
7 | P & F of Heavy Duty Sloated Angle Racking System 600mm deep. of approved Brand ( For Fabric Storage) | SQFT | 600 |  | 0
8 | P & F of Heavy Duty Sloated Angle Racking System 1550mm deep. of approved Brand ( For Fabric Storage) | SQFT | 300 |  | 0
9 | Supply & Installation of 2440x1200mmx1200mm Cutting, & Finishing Table with MS Basket below the table. | NO | 3 |  | 0
| TOTAL (D) |  |  |  | 0

## PARTATION.CEILING
CEILING,PARTITIONS,WALLS & FINISHES (J)
S.No | DESCRIPTION | MAKE | UNIT | QTY | RATE | AMOUNT
(A) | CEILING
1 | GYPSUM BOARD CEILING : Providing and fixing suspended type gyp board plain false ceiling firmly fixed on GI framework section all similar to specification of CIB Steels as detailed below:ii) Perimeter channel (MF6A) 20mm x 27mm all along the wall fixed with the help of nylon selvees and screws @ 600 mm c/c. ii) Intermediate channel (MF7) 15mm x 45mm x 0.9mm at 1200mm c/c. iii) Ceiling angle 25mm x 10mm x 0.55mm thick fixed to soft with GI cleat and steel expansion anchor fasteners. iv) Ceiling channel (MF5) 80mm x 26mm x 0.5mm @ 450mm c/c. v) 12mm thick plain Gypsum board is fixed to the ceiling section with 25mm drywall screws @ 230mm c/c. finally boards are to joined and finished so as to have flush look and leveling the board so as to be in one single plane which includes filling and finishing the board edges with jointing compound, paper tape. complete as per Design. | Gyproc (Board Only) | SQFT | 200 |  | 0
2 | MODULAR GRID CEILING ‐ Providing & Fixing of 600 x 600mm Mineral Fiber, Suspended Ceiling System : Fine fissured (RH ‐ 99) micro look. INSTALLATION:To comprise main runner spaced at 1200mm centres securely fixed to the structural soffit by approved hangers at 1200mm maximum centre & not more than 150mm from spliced joints. The last hanger at the end of each main runner should not be greater than 600mm from the adjacent wall. 1200mm long cross tees to be interlocked between main runners at 600mm centre to form 1200 x 600 mm module. Cut cross tees longer than 600mm require independent support. 600 x 600mm module to be formed by fitting 600mm long cross tees centrally between the 1200 mm cross tees. The 1200mm cross tees to have central ”birdsmouth” notches to facilitate fitting of 600mm cross tees. Wall angles in white colour to be secured to walls at 450 mm maximum centres. Location: Office areas | AMF/ ArmStrong | SQFT | 0 |  | 0
B | PARTITIONS AND WALL
1 | FULL HEIGHT GYPSUM PARTITION (75MM THICK) :‐ GYPSUM BOARD PARTITION‐P/F 75mm thick gypsum board partitions ,consisting Two layer of tapered edge 12.5mm thick,1200mm wide gypsum plaster board (conforming to IS 2095 ‐ 1982) on both sides of GI stud (CIB Steel), screws fixed with dry wall screws of 25mm at 300 mm centres with joints scattered, 48mm metal studs to be (0.5 mm thk. having one knurled flange of 34 mm and with joints scattered and another knurled flange of 36mm fabricated from G.I. sheets) placed in 50mm floor and ceiling channels @ 600 mm centres, floor channel fixed to concrete soleplate, and ceiling channel fixed to concrete soffit by nylon raw/ plugs @600 mm c/c, p/fixing of edge beads, corner protection angle bead, p/f kail wood frames for door frame / storages/cutting for electrical boxes etc. complete. | Gyproc (Board Only) | SQFT | 400 |  | 0
2 | FULL HEIGHT ALEMINIUM PARTITION (75MM THICK) :‐ P & f of 18g Heavy Duty Alum Partation lower side coverd with 12mm thk prelaminated Board & above 1200mm ht. Fixed with 6mm th. Tuff glass. Including Door shutters. | Jindal | Rate only |  |  | 0
3 | ALEMINIUM DOORS : P & F 18G HEAVY DUTY Alum. Door with Door Frame including 12mm Prelaminated Board & 6mm thk. Tuff Glass complete with all fitting and hardware. Door size 1000/1200x 2400mm | NO | Rate only
( C ) | FINISHES
1 | POP PUNNING ON WALLS Providing and rendering 10 mm thick Pop plastering on all walls surfaces in two layers consisting of plaster of paris with water ,forming key to receive the finishing coat including necessary scaffolding and curing etc. Complete at all heights till false ceiling. |  | SQFT | 300 |  | 0
2 | Plastic emulsion paint on walls and gypboard ceiling including surface preparation, primer coats, leveling patti and minimum 3 coats of brush and roller finish. | ICI Delux/ Asian / Berger / Nerolac | SQFT | 15300 |  | 0
3 | Texture paint:‐providing and applying texture paint on wall of approved brand and manufacturer after scrapping, having the existing finish and applying primer coat. ( Basic rate of Texure paint Rs. 40/‐ per Sq.ft ) | ICI Delux/ Asian / Berger / Nerolac | SQFT | 0 |  | 0
4 | Accent colour paint : Providing and applying Accent colour paint on wall and ceiling as approved by the architect, including all grooves etc. complete as directed. Rs. 50/‐ per Sq.ft ) | ICI Delux/ Asian / Berger / Nerolac | SQFT | 0 |  | 0
5 | DUCO paint : Duco paint on MDF panels as approved by the architect, including all hardware, grooves etc. complete as directed. | ICI Delux/ Asian / Berger / Nerolac | SQFT | 0 |  | 0
6 | P & F of Vinayl Digital Print. |  | SQFT | 300
7 | P & F of Frosted Glass Film |  | SQFT | 200
| Total FINISHES |  |  |  |  | 0

## CCTV & NETWORKING WIRING
CCTV & NETWORKING WIRING (H)
S.no | Item | Featrures | Make | Unit | Rate | Amount
1 | Dome/Bullet camera (In Door) | CP-Plus 1.3MP HDCVI IR Camera, IR With 3.6mm Fixed Lens, 1/3” Day/Night Vision (Range upto 10-15 Meter) | CP PLUS | 24 |  | 0
2 | Digitle video recoder (Full HD 1080p) | *32 Port CP-Plus DVR *Resolution 1080p * 4SATA Port. 2USB, 1RJ45 *HDMI/VGA video output *Mobole software: icmob,gcmob,wcmob *CMS Software : KVMS,KVMSpro | CP PLUS | 1 |  | 0
3 | Power supply (ERD ) | Power Supply For 32 Camera | CP PLUS | 1 |  | 0
4 | Conneters | BNC/DC(per camera 3pec) |  | 72 |  | 0
5 | Hard disk | 4tb (surveillance wd ) | SEAGATE | 1 |  | 0
6 | CCTV wiring | Wire (3+1 solid copper ) | CP PLUS | 529 |  | 0
7 | Installation | Camra & DVR |  | 24 |  | 0
8 | Networking wiring | CAT 6 per mtr | D LINK/FINOLEX | 900 |  | 0
9 | EPABX | Panasonic KXTES824BX Epabx System, Equipped With 06Trunk Line+24 Analog Extn, Party conference, Call waiting, Call forwarding with all latest features and many more.(Expandable upto8*24) |  | 1 |  | 0
10 | Caller-ID | Panasonic Caller-Id Card For System |  | 1 |  | 0
11 | Operating Console | Panasonic Digital Phone/Operating Console, Model No. KXT-7730X |  | 1 |  | 0
12 | MDF Box | MDF Box 50 Pair With Krown Module & Krown Strip With All Connectors & Cables |  | 1 |  | 0
13 | Installation | Installation & Commissioning Charges |  | 1 |  | 0
|  | CARRIED TO SUMMARY |  |  |  | 0

## FIRE FIGHTING SYSTEM
FIRE FIGHTING SYSTEM ( C )
S.No | DESCRIPTION | UNIT | QTY | RATE (Rs.) | AMOUNT
A | Fire Alarm And Detection System
1 | Providing & Fixing of fire alarm control panel fabricated from 16 SWG CRCA sheet toaccommodate for zones as required I/C testing ofeach circuit separately for resetting complete withpainting as required as per the specification 04 ZONES
| Make :- AGNI / Agni Suraksha( ASES) / APS | Each | 1 |  | 0
2 | Providing & Fixing of manual call box 16 gauge insuitable enclosure with arrangements to raise thealarm when the glass in manually broken complete
| Make :- Agni Devise / ASES | Each | 4 |  | 0
3 | Providing & Fixing of electronic hooter suitable for mounting complete as required including
| Make :- Agni Devise / ASES | Each | 4 |  | 0
4 | Providing & Fixing of Smoke Detector suitable for mounting complete as required including
| Make :- Apollo / System Sensor/Agni | Each | 30 |  | 0
5 | Providing and fixing copper armored cables 1.1 KVA grade including necessary support clamps at ceiling level and connection legs complete in all respects.
Make :- Finolex / Polypack
a | Control cable 2 core 1.5 Sq.mm | Metre | 900 |  | 0
6 | Providing and fixing Carbon-di-oxide fire extinguishers consisting of welded M.S.cylindrical body, extinguishers consisting of welded M.S.cylindrical body, extinguishers consisting of welded M.S.cylindrical body, tube, 30cms long high pressure discharge hose,discharge nozzle, suspension bracket,confirming to IS : 934 finished externally withred enamel paint and fixed to wall with brackets with rawl plug/dash fastenerscomplete with internal charge.(I.S.I. Marked)
Make :- Spectra fire / Safeguard / Greatex
a | Capacity-4.5 kg. | Each | 4 |  | 0
7 | Providing and fixing ABC type dry powder extinguisher as per New IS :15686 consistingof welded MS cylindercal body ,with dischargevalve, nozzle hanging arrangement complete .
Make :- Spectra fire / Safeguard / Greatex
| Capacity - 4 Kg | Each | 4 |  | 0
8 | Providing and fixing led light type exit signage. | Each | 4 |  | 0
| Total |  |  |  | 0

## ELECTRICALS
ELECTRICALS (G)
S. No. | Description | Unit | Qty. | Rate | Amount
(A) | POINT WIRING
POINT WIRING : Point wiring rates are inclusive of 2x2.5 +1x1.5 sq mm FR PVC insulated stranded copper conductor wires for circuit and 1.5 sq mm FR FR PVC insulated copper conductor insulated earth wire.
1 | Wiring for the following light/fan points with 3x1.5 Sq.mm FR PVC insulated stranded copper conductor wires in concealed FR PVC conduits in F.ceiling/walls/ceiling as direc-ted including providing 6 amps flush type switches, 5 sided G.I Boxes for housing switc-hes and earth-ing comple-te as required.
a. | Light Point | Nos. | 173 |  | 0
b | FAN Point | Nos. | 50 |  | 0
2 | Wiring for projector points with 2 x 2.5 + 1 x 1.0 sq mm FR PVC insulated stranded copper con-ductor wires in concealed FR PVC conduits in ceiling/ walls/ Ceiling as directed including providing 16 amps flush type switch near the white board and 16 amps 5 pin socket near the projector in ceiling , 5 sided G.I. boxes for housing switches and 16 amps 3 pin socket outlet and earthing and complete as required.(including body earth for GI boxes) (1 point per circuits) | Nos. | 6 |  | 0
3 | Wiring for 10 amps power outlet poi-nts with 2 x2.5 sq.mm FR PVC insulated stranded copper conductor wires in concealed/recessed FR PVC conduit as directed including providing 16 amps flush type switch and 6 pin socket with cover plate 5 sided G.I. outlet boxes for switches and socket and earthing the third pin with 1.0 sq mm FR PVC stranded copper wire complete as required (Only one outlet shall be connected on each circuit) (including body earth for GI boxes) | Nos. | 60 |  | 0
4 | Wiring for 16 amps power outlet poin-ts with 2X4 sq.mm FR PVC insulated stranded copper conductor wires for the first power outlet and 4 sq.mm FR PVC insu-lated stranded copper conductor wires for the second outlet, in concealed FR PVC cond-uits in F.ceiling/ walls/Ceiling/floor ducts as directed incl-uding providing 16 amps flush type switch and 6 pin socket with cover plate, 5 sided G.I. outlet boxes for housing switches and sock-et, and earthing the third pin with 2.5 sq.mm FR PVC insulated copper conductor wires complete as required (Two power out-lets shall be connected on each circuit)(including body earth for GI boxes) | Nos. | 24 |  | 0
5 | Wiring for 40 amps three phase power outlet poin-ts with 3X10 sq.mm FR PVC insulated stranded copper conductor wires power outlet and 10 sq.mm FR PVC insu-lated stranded copper conductor wires for the second outlet, in concealed FR PVC cond-uits in F.ceiling/ walls/Ceiling/floor ducts as directed incl-uding providing 40 amps TPN MCB G.I. outlet boxes for housing FR PVC insulated copper conductor wires complete as required (Two power out-lets shall be connected on each circuit)(including body earth for GI boxes) | Nos. | 6 |  | 0
6 | Wiring for UPS/Raw plug outlets points with three core, 2.5 sqmm FR PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS : 694/1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor inclu-ding all cable termination accessories) Earthing of GI Box to be included | RM | 450
7 | Wiring for UPS plug outlets points with three core, 10.0 sqmm FR PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS : 694/1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor inclu-ding all cable termination accessories) | RM | 200
8 | Wiring for A/C outlet points with 2X4.0 sq mm FR PVC insulated stranded copper conductor wires in FR PVC conduitl/wall/floor ducts as directed including providing 25 A socket with 25 amps SP MCB ( Tiny Trip) 5 sided GI Outlet Box for housing and socket and MCB and earthing with 2.5 sq. mm FR PVC insulated stranded Copper Conductor wires complete as required. | RM | 310
The word RAW shall be engraved on all RAW sockets
a. | 3 pin 16/20 A 1 phase industrial socket with plug top | Nos. | 60 |  | 0
b. | 3 pin 32 A 1 phase industrial socket with plug top IP65 | Nos. | 6 |  | 0
c. | 3 pin 20 A 1 phase industrial socket with interlocking switch and plug top | Nos. | 20 |  | 0
8 | Providing and fixing in position the following FR PVC conduits including all accessories concealed in F. ceiling/wall/floor as required including 1.6 mm thick M.S. junction or pull boxes with 3mm thick perspex sheet cover plate compl-te with 1.6 mm dia. G.I. pull wires in the length of conduit.
a. | 20 mm dia conduit ( 1.6 mm thick) | RM | 200 |  | 0
b. | 25 mm dia conduit (1.6 mm thick) | RM | 325 |  | 0
c. | 32 mm dia conduit (2.0 mm thick) | RM | 100 |  | 0
9 | The Electrical Contractor shall provide sufficient temporary lighting for working in the Building total area 8661.8 sq. ft. divided in 1 floors and maintain the same till completion of the project.It shall include replacement of all fused/faulty lamps.It shall include providing 16 A plug sockets (industrial type with ON/OFF switch/MCB) on 4 sides walls one plug at every 3 meter distance. The Contractors will tap off supply from these plugs for his use. Halogen/tubelights to maintain a lighting level of 150 lux on the floor,.Each 15 A socket and each Light circuit shall be protected by suitable MCBs.Use three core PVC Insulated PVC sheathed copper conductor cables for wiring.The contractor shall salvage the complete wiring and take it back at the end of the project. | L.S. | 1 |  | 0
(B) | CONDUITING FOR TELEPHONE , COMPUTER & CONDUITING AND WIRING FOR T.V. SYSTEM.
1 | Providing and fixing in position the following FR PVC conduits including all accessories concealed in F. ceiling (PVC conduit not to be installed above false ceiling)/wall/ floor as required including M.S. junction or pull boxes with 3mm thick perspex sheet cover plate complete with 1.6 mm dia G.I. pull wires in the length of conduit.
a. | 20 mm dia conduit | RM | 125 |  | 0
b. | 25 mm dia conduit | RM | 250 |  | 0
c. | 32 mm dia conduit | RM | 175 |  | 0
2 | Providing and fixing in position the following PVC flexible G.I Wire reinforced conduits including all fixing accessories on to the modelur furniture
a. | 25 mm dia flexible conduit with end couplers | RM | 150 |  | 0
3 | Providing and fixing in position suitable 1.2 mm thick G.I./ PVC outlet box for RJ- 45 computer outlet with all fixing accessories as required. | Nos. | 30 |  | 0
4 | Supply and Laying including numbering / ferruling of wire (8 digit) and the continuity test for each cable of Cat 6 - Telephone / Data cable in existing G. I. Channel. | RM | 600 |  | 0
5 | Providing and fixing in position suitable 1.6 mm thick G.I. outlet box for 2 nos RJ - 45 for Data/ voice outlet including crimpling with all fixing accessories as required. | Nos. | 30 |  | 0
6 | Providing and fixing in position suitable 1.6 mm thick G.I. outlet box with 1 no RJ - 45 for Data/ voice outlet including crimpling with all fixing accessories as required. | Nos. | 30 |  | 0
7 | Supply and fixing of 1.6 mm thick G.I Box along with RG 11 TV Co axial socket with Cover Plate | Nos. | 6 |  | 0
8 | Supply drawing connecting testing and commissioning of TV Coaxial cable RG 6 in existing conduit | RM | 200 |  | 0
( C ) | SUPPLY & FIXING OF LIGHTING FIXTURES
Supplying ,fixing in position testing and commissioning of the following Lighting fixtures including lamps at site. . Use all Philips Trulite/Osram lumilux plus Eco lamps in Fluorescent lamp fittings. ( 4000 K) Use Osram CFL lamp - Dulux L Lumilux in all Flurosent lamp fixtures (4000 K) (Samples of all light fixtures to be submitted to the client for approval prior to procurement of fixtures)
Note | All Light Fixture shall be with H.F. electronic ballast ( THD less than 10% and P.F. 0.995 )
1 | Proving & fixing of 1 x 24 watts, 3000K/4000k/6500k LED down light in Round/Square shape in 150mm dia Size 1200x150mm | Nos | 40 |  | 0
2 | Providing & fixing of 2x28 Watts 1200x200mm Light Fixture 6500K/4000k/3000k (standard make) Note: Philips/syska/havells charges extra | Nos | 115 |  | 0
3 | P & F of 15w Led Down Light Fixture 1500mm dia surface Mounted. | Nos | 36 |  | 0
4 | LED Strips for Cove Light in philips/havells/Wipro | Rmt | 90 |  | 0
5 | P & F of 56" dia Ceiling Fan | Nos | 60 |  | 0
(D) | CABLES ,MAINS & SUBMAINS
1 | Supply and laying, effecting proper connec-tions, testing & commissioning of the following sizes of 1.1 KV XLPE armoured/ unarmoured PVC insulated PVC sheathed aluminium/copper conductor cables conforming to IS : 1554 and IS 694 for Flexible copper cable Part I - 1976 with latest amendments laid over MS supports in existing RCC ducts/ laid in ground /laid on Cable Trays including clamping the cables to sup-ports in an approved manner as required complete with all accessories. including heavy duty copper terminal crimping lugs, solder, insulation tape, approved sealing epoxy compound, double compression brass cable glands, effecting gland connec-tions and effecting terminal connections to the equipment complete as required.
d. | 3.5 c x 185 sq.mm XLPE armourd aluminium conductor cable | RM | 90
e | 3.5 c x 95 sq.mm XLPE armourd aluminium conductor cable | RM | 40
f. | 3.5 c x 70 sq.mm XLPE armourd aluminium conductor cable | RM | Rate Only
g. | 3.5 c x 50 sq.mm XLPE armourd aluminium conductor cable | RM | Rate Only
h. | 4 c x 25 sq.mm XLPE armourd aluminium conductor cable | RM | 60
i | 4 c x 16 sq.mm armoured copper cable for UPS, Light and power DB's | RM | 25
j | 4 c x 10 sq.mm armoured copper cable | RM | Rate Only
k | 4 c x 6 sq.mm armoured copper cable for A.HU | RM | Rate Only
l | 4 c x 4 sq.mm armoured copper cable | RM | Rate Only
m | 3 c x 4 sq.mm armoured copper cable | RM | Rate Only
n | 2 c x 16 sq.mm PVC insulated unarmoured copper conductor cables | RM | Rate Only
o | 2 c x 10 sq.mm PVC insulated unarmoured copper conductor cables | RM | Rate Only
( E ) | (TRUNKING AND CABLE TRAYS
1 | Fabricating supplying to site of installation, installation on ceiling/ (Salamandre® standard and IP4X distribution trunking), totally enclosed, the joints between two lengths of channels or between channel and junction box shall be joined together with MS coupler plates to make it dust and water proof. The cost shall including all supporting and fixing accessories including dash fasteners. Make (Salamandre® standard and IP4X distribution trunking) LEGRAND Make
a. | 75 mm (wide) x 50 mm (height) | RM | 90 |  | 0
b. | 100 mm (wide) x 50 mm (height) | RM | 95 |  | 0
d. | 55 mm (wide) x 40 mm (height) | RM | 45 |  | 0
2 | Design manufacture , supply and fixing in position the cable trays of the following sizes for supporting 1.1 KV grade armoured/unarmoured aluminium /copper conductor cables. Fabricate the cable trays from perforated 1.6/2mm thick M.S. CRCA sheet duly galvanised with expansion coupler plates duly galvanised, with bolts, washer and nuts. Knock out holes for cable connections as per approved design. The tray should comply with the specification of NEC (National Electric Codes) and NEMA (National Electric Manufacturers Association). The steel should be as per IS:226 and galvanising as per IS : 2629/BS 729/ASTM 123. The rate shall also include for supporting steel , fish plates , fixing accessories , nuts bolts, supporting down rods , dash fastener, cutting the RCC etc. complete as required. (the horizontal and vertical bends, T's should be factory fabricated and the rate should include for the same)
a. | 150 mm wide x 40 mm x 1.6 mm thk | RM | 60 |  | 0
b. | 300 mm wide x 40 mm x 2.0 mm thk | RM | 100 |  | 0
(F) | DISTRIBUTION BOARDS
(NOTE: ACTUAL COMPONENTS MAY VARY AFTER FINAL DRAWINGS)
Supply,inginstalling ,connecting testing and commissioning of the following double door 1/4 rows vertical type 1.6 mm thick and 1.4 mm thick door sheet steel enclosed fully recessed type, TPN Miniature Circuit Breakers Distribution Boards dust proof, verm-in proof, with hinged and lockable doors complete with DP MCB's and inter-connection with copper wires, or copper tapes, cable glands-/conduit entry bushes, bonding to earth and painting. Also provide separate neutral busbar for each phase. Provide separate Earth Links. Use brass thimbles for connections of all wires. 1 row for single phase and 4 rows for 3 phase. Provide separate 4 way 63 A main neutral link also.
1 | Light & Power Distribution Board
a | 12+2 Way TPN DB, each phase consisting of 10 Nos. 10/20 AMP SP MCB’s and controlled by one number 100 mA sensitivity 63 AMPS DP RCCB backed up with 1 no 63 Amps 4 pole MCB. | Nos.. | 2 |  | 0
b | 12+2 Way TPN DB, each phase consisting of 10 Nos. 10/20 AMP SP MCB’s and controlled by one number 63 AMPS DP MCB for each phase and 1 no. 63 amps 4 pole MCB incomer | Nos.. | 2 |  | 0
c | Supply, installation, testing and commissioning of sheet metal enclosed 150KWA Electrical Penal With Bus Bar, Cable ally, AMF Penal for Genset, 150amp Incommer MCCB, and 6 no. of 40 to 100 amp. Outgoing MCCB, and 6 no. TPN of 32 to 63 amp. Complete including termination of all cables. | Nos. | 1 |  | 0
| SUB TOTAL A+B+C+D+E+F |  |  |  | 0

## FURNITURE
FURNITURE (K)
S. No. | Description | Unit | Qty. | Rate | Amount
(A) | OFFICE FURNITURTE
1 | WORK STATIONS
1 | Workstation 5' x 2' x 2'-6" high | Nos. | 4 |  | 0
| PARTITION - 50MM TO 60MM THK. PANEL BASED SYSTEM WITH Coloured lacured glass |  |  |  | 0
| TABLE TOP : 25MM THK TABLE TOP WITH PVC EDGE BANDING |  |  |  | 0
| PEDESTAL UNIT : 1DRAWER+1FILING UNIT ON CASTOR, SIZE 400 X 470 X 525MM |  | 4 |  | 0
2 | CHAIRS
a | STAFF CHAIR BSP@ 4000/- |  | 12 |  | 0
b | CABIN CHAIR@ BSP@ 9000/- Each |  | 4 |  | 0
(B) | LOOSE FURNITURE
1 | RECEPTION
a | RECEPTION COUNTER Size 2000x600x750mm Made of 18mm Thk. Commercail Ply Wood & Finish with approved Laminate, as per design. |  | 1 |  | 0
b | 3 SEATER SOFA BSP@ 18000/- each |  | 1 |  | 0
e | SIDE TABLE BSP @ 4500/- each |  | 1 |  | 0
2 | PRINCIPAL AREA
a | TABLE WITH SIDE TABLE : Size 2100x900mm Made of 18mm Thk. Pre Laminate/Commercail Ply Wood & Finish with approved shade of Lamiante as per design. |  | 1 |  | 0
0
3 | COMPUTER TABLE |  |  |  | 0
| 1200X600X750MM |  | 2 |  | 0
0
4 | LAB/CLASS ROOM CAHIR WITH WRITING PAD |  | 24 |  | 0
| Model no. GST 807 (Geeken) BSP@ 4000/- |  |  |  | 0
5 | MASTER CHAIR BSP Mediam Height |  | 6 |  | 0
| Model no. GC 9006 (Geeken) BSP@ 6000/- |  |  |  | 0
| (B) CARRIED TO SUMMARY |  |  |  | 0

## AIR CONDITIONING
AIR CONDITIONING (D)
S. No. | DESCRIPTION OF ITEM | UNIT | QTY | RATE | AMOUNT | Qunatity | Amount
A | AIR WASHER
Supply, Installation, Testing and commissioning of Air-Washers having double skin housing inner panel 0.6 GI plain sheet and outer panel shall be 0.6 mm precoated GI with 25 mm PUF 40 kg/cuM, with stainless steel tank made out of 18 G stainless steel, forward curved DIDW Centrifugal blowers(AMCA certified), complete with TEFC Sq. cage induction motor IP-55, IE-2, Monoblock pumpset for water circulation, G.I B class/PVC piping, Aluminium metallic filters in G.I frame, 200 mm. thick Cellulose pads of imported origin complete as per specifications. Fire proof double layered canvass cloth connection for outlet complete with flanges made out of 20G G.S.S sheet on both sides for connection to air washer and duct complete with nuts, bolts etc. as per specification. The air washer shall be complete with water inlet, drain & overflow connections with valves and vibration isolation arrangment.
Capacity Static Pressure
i | 9000cfm 40mm WG | Nos. | 2 |  | 0
B | Fresh Air Duct Work (AIR WASHER)
1 | Supply, Installation, Testing Balancing & Commissioning of the following items as per approved working drawings, specifications and requirement
G.S.S Round/rectangular factory fabricated ducting complete with gaskets, elbows, splitters, vanes, supports etc. as per drawings and as required for air distribution.
a) | 24 G | SqM | 75 |  | 0
b) | 22 G | SqM | 50 |  | 0
c) | 20 G | SqM | 25 |  | 0
2 | SUPPLY AIR GRILLE
| Supply, installation, testing and balancing of Supply Air Rectangular Grilles with volume control damper, with frame made out of powder coated extruded aluminium sections complete with wooden frame, gasket screws, etc. as specified. | SqM | 2 |  | 0
3 | DUCT VCD
| Supply, fabrication, installation and testing of opposed blade G.I. construction Box type duct volume control damper complete with nuts bolts, screws, linkage, flanges etc.ducts lever and quadrants for proper balancing of the air distribution system as per specifications and drawings. | SqM | 1 |  | 0
4 | DUCT INSULATION
Supply , installation , testing and commissioning of external thermal insulation on ducts with Closed Cell Cross Linked Polythylene (XLPE) Al. Foil Faced Foam of density 33 Kg/m³ with 12 mm thermal Conductivity not exceding 0.035 W/mK at an average Temperature of 40°C. The Material Shall be rated as Class 1, As per BS476 Part 7 , The Smoke Density as per AS - 1530.3 Shall not exceed 1. The Material shall have Fire Approval from Govt of India Lab & no toxicity under flaming and non- flaming condition as per AITM 3.000 (1993) . Adhesive used for setting the insulation shall be non - flammable, Vapour Proof (SRX-PRES-PIDILITE). All Joints should be sealed with 3 mm thick 50 mm wide PE tape and Flange to be overlapped by 6" width of the same material thickness. Finally insulated duct shall be strapped by 12 mm Plastic Packing strip at every random meter and conforming to Specification
i | 6mm thick | SqM | 150 |  | 0
C | ELECTRICAL WORK (AIR WASHER)
1 | Supply, Installation, Testing and commissioning of Starter Panels near the scrubber constructed out of 2mm thick CRCA sheet duly powder coated as per specifications. The panel shall have hinged door with on-off interlocks. The panel shall be complete with incoming MCCB/MCB, suitable bus bars of aluminum construction, bus links complete with direct online starter/Star-delta starter with 'hands", "off", automatic mode selection switch, ammeter for each motor, timer, Auto Manual switch, remote start/stop contacts, potential free contacts for switch off Air Washer in case of fire, earthling connector etc., as required complete as per specifications. The panel shall be suitable for outside installation.
Air Washer panel shall have the following:
Indicating lights LED for incommer and outgoing
Ammeter with selector switch
Volt meter with selector switch with fuse
Panel With following Capacities:
For 9000 CFM Air Washer
Incoming/Outgoing
i | 32 Amp 10 kA TP MCB complete with Direct On Line- 1 x 5.5 kW suitable for connections 1x3Cx10 sq.mm XLPE cable & feeder with 10 Amp MCB & starter for pump. | No. | 1 |  | 0
2 | Supplying, laying, effecting proper connec­tions, testing & commissioning of the following sizes of 1.1 KV -Cross Linked Poly Ethelene armoured aluminium conductor cables conforming to relevant latest amended Indian Standards laid over MS supports & Cable Trays duly painted including clamping the cables to supports in an approved manner as required complete with all accessories.
i | 3C x 10 sq.mm | RM | 50 |  | 0
ii | Supplying, laying, effecting proper connections, testing & commissioning of the Copper Flexible Cable 3x2.5 Sqmm complete with fixing arrangment etc all complete as required. | RM | 50 |  | 0
3 | Supplying, laying, effecting proper connec­tions, testing & commissioning of following sizes of GI earthing Strip/Wires including fixing clamps and effecting proper connections to equipment etc. complete as required.
a | 10 SWG G.I. Wire | RM | 50 |  | 0
D | CABINET TYPE EXHAUST FAN
Supply, installation, testing, and commissioning of Double skin casing construction of 0.6 mm thick GI plain sheet inner and outer panel Precoated with 25mm thk Puf insulation 40 kg/cum density, exhaust air fans comprising of DIDW Centrifugal Blower Class I construction complete with TEFC sq. cage induction motor, IP-55 protection IE-2, mounting frame work to mount fan & motor, V- belts, pullyes, belt guard, all complete as required . The motor shall be suitable for 3 phase, 415 volts, 50 Hz supply. The unit shall be complete with vibration isolators.
Capacity Static Pressure
i | 4000cfm 30 mm WG | Nos | 3 |  | 0
E | Duct Work (EXHAUST FAN)
1 | Supply, Installation, Testing Balancing & Commissioning of the following items as per approved working drawings, specifications and requirement
G.S.S square/ rectangular site fabricated ducting complete with gaskets, elbows, splitters, vanes, supports etc. as per drawings and as required for air distribution.
a) | 24 G | SqM | 110 |  | 0
b) | 22 G | SqM | 65 |  | 0
2 | EXHAUST AIR GRILLE
| Supply, installation, testing and balancing of Exhaust Air Rectangular Grilles with volume control damper, with frame made out of powder coated extruded aluminium sections complete with frame, gasket screws, etc. as specified. | SqM | 3.4 |  | 0
3 | DUCT INSULATION
Supply , installation , testing and commissioning of external thermal insulation on ducts with Closed Cell Cross Linked Polythylene (XLPE) Al. Foil Faced Foam of density 33 Kg/m³ with 12 mm thermal Conductivity not exceding 0.035 W/mK at an average Temperature of 40°C. The Material Shall be rated as Class 1, As per BS476 Part 7 , The Smoke Density as per AS - 1530.3 Shall not exceed 1. The Material shall have Fire Approval from Govt of India Lab & no toxicity under flaming and non- flaming condition as per AITM 3.000 (1993) . Adhesive used for setting the insulation shall be non - flammable, Vapour Proof (SRX-PRES-PIDILITE). All Joints should be sealed with 3 mm thick 50 mm wide PE tape and Flange to be overlapped by 6" width of the same material thickness. Finally insulated duct shall be strapped by 12 mm Plastic Packing strip at every random meter and conforming to Specification
i | 12mm thick | SqM | 90 |  | 0
F | ELECTRICAL WORK (Exhaust Fan)
1 | Supply, Installation, Testing and commissioning of Starter Panels near the airwasher constructed out of 2mm thick CRCA sheet duly powder coated as per specifications. The panel shall have hinged door with on-off interlocks. The panel shall be complete with incoming MCCB/MCB, suitable bus bars of aluminum construction, bus links complete with direct online starter/Star-delta starter with 'hands", "off", automatic mode selection switch, ammeter for each motor, timer, Auto Manual switch, remote start/stop contacts, earthling connector etc., as required complete as per specifications. The panel shall be suitable for outside installation.
Exhasut Fan panel shall have the following:
Indicating lights LED for incommer and outgoing
Ammeter with selector switch
Volt meter with selector switch with fuse
Panel With following Capacities:
For 6200 CFM Exhaust Fan
Incoming/Outgoing
i | 32 Amp MCB TPN 10 kA complete with DOL STARTER- 1 x 3.7 kW suitable for connections 3Cx10 sq.mm XLPE cable. | No | 1 |  | 0
2 | Supplying, laying, effecting proper connec­tions, testing & commissioning of the following sizes of 1.1 KV -Cross Linked Poly Ethelene armoured aluminium conductor cables conforming to relevant latest amended Indian Standards laid over MS supports & Cable Trays duly painted including clamping the cables to supports in an approved manner as required complete with all accessories.
i | 3C x 10 sq.mm | RM | 45 |  | 0
3 | Supplying, laying, effecting proper connec­tions, testing & commissioning of following sizes of GI earthing Strip/Wires including fixing clamps and effecting proper connections to equipment etc. complete as required.
a | 10 SWG G.I. Wire | RM | 45 |  | 0
G | Ceiling Mounted Cassette Air Conditioner
1 | Supply, Installation, Testing and Commissioning of the following equipment as per tender drawings, and specifications. (For office & Class Room)
a | Daiken 2.8ton Cassette Type 3* Rating | no. | 2
b | Copper flexible connection complete with set of brass ball valves, one valve with and one valve without strainer. | rmt | 60
c | Installation charges | no. | 2
d | 25mm PVC Dran Pipe with Insulation | mtr | 40
H | TOILET EXHAUST FAN
1 | Supply, Installation, Testing and commissioning of Rectangular/Circular type Exhaust air fan 20G GSS comprising of centrifugal fans complete with direct driven induction motor, metal clad MCB & starter 15 m length cable, earthing, all compete as required, suitable for single phase, 230 volts, 50Hz AC. supply of following capacity:
i | 1000 cfm SP-25mm | Nos. | 1
TOTAL |  |  |  |  | 0